        & industrie 4.0
Plan
1. LoRaWAN et Modbus
2. Autres capteurs LoRaWAN
3. Exemples

---
I. LoRaWAN & Modbus

---
Quelques fabricants Français
- https://ewattch.com/
  Saint-Dié-des-Vosges
- https://www.watteco.fr/
  Hennebont
- https://www.atim.com/
  Villard-de-Lans

---
Solution proposée par eWattch

---
eWattch Tyness + module Modbus
Esclave Modbus
Maître Modbus
RS485 Half Duplex

---
Modbus sur RS485
requête
- Plusieurs câblages RS485
  - Full duplex
    - 4 fils : Tx+ Rx+ Tx- Rx-
    - Point à Point
      (1 seul esclave)
    - Peu utilisé industriellement
  - Half duplex
    - 2 fils : A+ B-
    - Multipoints
      (plusieurs esclaves)
    - Très utilisé
    - NB : Rt en fin de bus
Tx+
Rx+
v(t)
Rx-
Tx-
Rx+
Tx+
v(t)
Rx-
Tx-
réponse
Esclave
Maître
Requête puis réponse
v(t)
Rx+
Rx-
A+
A+
Tx+
B-
B-
Tx-
Maître
Esclave 1
Esclave 2

---
Compléter câblage Tyness Modbus
Extrait doc Twido
Extrait doc Tyness
A+
B-

---
Tyness Configurator.exe
Paramètres liaison série RS485
Micro USB
Mode Tyness
Période envoi Payloads
Config module
Profil et n° esclave

---
Ajout Profil
Requête modbus toutes les 10 s
Lecture à partir de l'adresse Modbus 0
Lecture de 3 mots
Non documenté et non prévu par le constructeur

---
Esclaves officiellement gérés par Tyness

---
function	manufacturer	reference	data
energy meter	Ewattch	Power Mid	full config: active and reactive power, imported as well as exported active and reactive energy, average line current harmonic distortion, mean line to neutral voltage || light config: energies only || power config: power and energies || volt amp energy config: voltage and current of every line and total energies
energy meter	Socomec	Diris A-40	total active and reactive power, total imported as well as exported active and reactive energy
energy meter	Socomec	Diris A-30/A-20/A-10	total active and reactive power, total imported as well as exported active and reactive energy
energy meter	Socomec	countis E50/E53	total active and reactive power, total imported as well as exported active and reactive energy
energy meter	Socomec	countis E43	total active and reactive power, total imported and exported active energy, total imported reactive energy
energy meter	Schneider Electric	PM710	total active and reactive power, total imported and exported active energy
energy meter	Schneider Electric	PM800	total imported as well as exported active and reactive energy
energy meter	Schneider Electric	PM3200	total active and reactive power, total imported as well as exported active and reactive energy
energy meter	Schneider Electric	PM5100	total active and reactive power, total imported as well as exported active and reactive energy
energy meter	Inepro	pro380	total and individual phases imported as well as exported active and reactive energy
energy meter	Elko	esmn	total active power and current, total active and reactive energy
air handling unit	Swegon	compact	airflows, fan speeds, temperature measures and setpoints, outdoor temperature, reheat level
energy meter	Socomec	I30	load 1, 2, and 3 active energy or load 1 active energy
energy meter	OTMetric	eFlex	total active and reactive power, total imported as well as exported active and reactive energy
heat meter	Micronics	U1000MKII	flow, volume, power, energy as well as flow and return temperatures
energy meter	Socomec	I60	load 1 and 2 positive and negative active energies and positive reactive energies
energy meter	Socomec	B30	total imported as well as exported active and reactive energy
energy meter	Schneider Electric	PM500	total imported as well as exported active and reactive energy
energy meter	Schneider Electric	micrologic NS(E/P/H)/NSX(Type E)/MTZ(Type E/P/H)	current of load 1, 2 and 3 as well as total imported as well as exported active and reactive energy
thermostat	heatmiser	edge heat	room temperature and setpoint
energy meter	Satec	PM130 plus	current and voltage of load 1,2 and 3 as well as total imported as well as exported active and reactive energy. Warning, the modbus table of the product should be configured in high resolution and integer
energy meter	Schneider Electric	IEM3000	total active and reactive power, total imported as well as exported active and reactive energy
Flow meter	VP Instruments	VPFlowScope	Flow, pressure, temperature, volume
energy meter	circutor	CVM C10	total imported as well as exported active and reactive energy
energy meter	circutor	CVM MINI	total imported as well as exported active and reactive energy
energy meter	circutor	CVM E3 MINI	total imported as well as exported active and reactive energy
heat meter	Prisma	DUS-CC-FC/DUC-TT-FC	inlet and outlet temperature, energy, and volume
energy meter	ABB	M2M	active energy and reactive energy
energy meter	lettel	map4 34rj	active energy load 1, load 2, load 3 and load 4

---
Autres solutions officielles eWattch
Demande d'intégration de nouveau capteur esclave Modbus : https://ewattch.typeform.com/to/IHSYFoM9
Alternative :
Automate en Maître
Tyness en Esclave

---
Visualisation sur le Network Server TTN
Gateway
Network
Server
Esclave
Modbus
Internet
Internet
LoRa

---
Décodage possible des trames sur TTN
EtatFeux (HEX little endian)
0050(hex) = 80(d)
cpt (HEX little endian)
0299(hex) = 665(d)

---
Serveur Applicatif AllThingsTalk

---
Serveur Applicatif AllThingsTalk

---
Visualisation sur smartphone

---
Règle d'alerte sur événement
Exemple
Dépassement d'un seuil sur le nombre de cycles du système

---
II. Autres capteurs LoRaWAN

---
Modules pour Tyness 1/2

---
Modules pour Tyness 2/2

---
Autres capteurs eWattch 1/2

---
Autres capteurs eWattch 2/2

---
III. Exemples

---
Consommation électrique
Puissance
Charge électrique
LoRa
SmartPlug
(device LoRaWAN)
Gateway
Serveur applicatif
Cayenne
MyDevice
Network
Server
LoRaWAN

---
Notification consommation anormale

---
Notification consommation anormale

---
Analyse vibratoire

---
Analyse vibratoire

---
Données de Bob Assistant